2ND WATER METER – RULES & REGULATIONS

(AREA MAINTENANCE METER)

- A heavy-duty “flare-to-iron pipe thread” fitting must be installed on the water lead from the street before any other fittings.

- NO SOLDERED JOINTS  are allowed before the first gate valve (A).

- NO GALVANIZED FITTINGS are allowed before the water meter.

- Piping & fittings after gate valve “A” can be either copper or brass (no galvanized).

- The tee for the area maintenance meter must be after the main valve & before gate valve “A”.

- Gate valves must be installed on both sides of both meters.

- Meters cannot be installed in a vertical position.

- Pressure reducers, when required, must be installed as shown on the diagram.

- There must be a minimum of 18 inches, but no more than 24 inches, between the domestic & area maintenance meters (see diagram).  Any variance requires written authorization from the DPW Director.

- A PLUMBING PERMIT IS REQUIRED. Please contact the Shelby Township building Department for permit information and fees at (586) 731-5969.

PLEASE REFER TO THE DIAGRAM (REVERSE SIDE OF PAGE)

The addition of a 2ND Water Meter allows us to apply the water-only rate to your outdoor water usage.

AVAILABLE METER SIZES:   ¾” (30 GPM) OR   1” (50 GPM)

To avoid an estimated bill, please call (586) 731-5990 for

remote & wire installation after the meter has been set !